{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":33,"n_cols":9,"rows_kept":33,"merged":[[0,0,0,6],[16,0,17,0],[16,1,17,1],[16,2,17,2],[21,1,28,1],[32,0,32,3]],"flags":["formulas_cached_only"]}
["国药集团动物保健股份有限公司悬浮培养灭活苗车间建设一期项目 "]
[null,"建筑单体","面积（㎡）",{"$nulls":3},"面积（㎡）","需提供的资料","丙类车间"]
[null,"总面积",23473.3]
["序号","检测类别","检测项目","建筑面积/检测数量","单价（元/㎡）","总价","备注"]
[1,"见证取样检测","钢筋及钢筋焊接件机械连接件力学性能、混凝土及砂浆抗压、混凝土抗渗、砂、石、水泥、墙体填充材料(不含保温材料)、砂浆配比、防水材料，回填土击实及压实度，道路材料、透水砖、直螺纹机械连接工艺性能检验、安全网、扣件，灌浆套筒抗拉性能等",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[2,"海绵城市","透水混凝土配合比验证、透水砖、透水板等",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[3,"主体结构检测","进场检测：现浇结构混凝土板厚检测、植筋抗拔检测、回弹法检测混凝土抗压强度检测、结构实体钢筋布置间距检测、钢筋保护层厚度检测。",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[4,"节能材料及现场检测","墙面及楼地面保温系统材料（保温材料强度、密度、导热系数、燃烧级燃烧；界面砂浆、抗裂砂浆拉伸粘结原强度、浸水后强度；玻纤网：经向、纬向耐碱断裂强力及保留率：塑料锚栓：单点锚固力）：屋面保温板材（保温板材强度、密度、导热系数、燃烧级燃烧）；建筑外窗及玻璃（外窗气密性、水密性和抗风压性能及传热系数，玻璃可见光透射比反射比遮阳系数及露点）；节能现场检测（外窗现场气密性、墙面保温厚度、墙面保温材料粘结强度、屋面、楼地面保温层厚度）",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[5,"水电材料及现场检测","电线电缆、给排水管材，绝缘电阻、防雷接地电阻、给水水压试验；通风空调通风检测要求对本项目地上部分及地下室进行通风检测（现场检测）",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[6,"装饰装修材料检测","内外墙乳胶漆、内外墙腻子粉、纸面石膏板、瓷砖、轻钢龙骨等",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[7,"室内环境检测","室内环境污染物氡、甲醛、苯、氨、TVOC含量检测",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[8,"防雷检测","防雷装置检测",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[9,"消防检测","消防设施检测",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[10,"绿色建筑","绿色建筑验收检测",23473.3,null,null,"按总建筑面积计算","可按建筑面积报价"]
[11,"玻璃幕墙","风压变形性能、雨水渗透性能、空气渗透性能、平面内变形性能",1,null,null,"幕墙性能检测及原材料检测均包含在内","没有幕墙没有此项报价"]
[12,"地基（筏板基础）","浅层平板荷载试验",14,null,null,"规范要求500㎡一个点","占地面积约6985.74 平方米，预估14个点"]
[13,"沉降观测","建筑物沉降观测",230,null,null,"观测","需要提供结构图","20个沉降点、3个基准点。观测10次"]
[{"$nulls":3},23,null,null,"布点"]
[14,"高压旋喷桩","桩身完整性（取芯）",60,{"$nulls":3},"2%且单位工程不少于6根，高压旋喷121根，每根约10m"]
[15,"支护桩","桩身完整性（低应变）",35,{"$nulls":3},"30%且不少于10根，116根，检测35根"]
[16,"检测项目","检测内容","数量","埋设单价","小计","监测单价","监测次数","小计"]
[null,"基坑监测","基准点",3,{"$nulls":3},30,0]
[null,null,"桩顶水平位移",25,{"$nulls":3},30,0]
[null,null,"桩顶竖向位移",25,{"$nulls":3},30,0]
[null,null,"坡顶水平位移",25,{"$nulls":3},30,0]
[null,null,"坡顶竖向位移",25,{"$nulls":3},30,0]
[null,null,"桩体变形","15孔/157.5米",{"$nulls":3},30,0]
[null,null,"重要建筑物监测",12,{"$nulls":3},30,0]
[null,null,"管线监测",11,{"$nulls":3},30,0]
[null,null,"道路沉降监测",32,{"$nulls":3},30,0]
[null,null,"小计",{"$nulls":5},0]
[null,null,"合计"]
["总计"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}